## Introduction
Sustainable Design Guidelines
Introduction: BAC aspires to remain an industry leader in sustainability. Sustainability is a way of life at BAC and sits at the heart of our business and plans to grow responsibly in a way that delivers positive outcomes to our customers, investors and the communities in which the airport operates. Purpose: The primary purpose of this guideline is to embed sustainability requirements into our capital investment programme in line with international best practices. The use of the checklist aims to strengthen sustainable outcomes across the project lifecycle and deliver our corporate sustainability targets through an aligned culture focussed on sustainability. The use of this guideline and it's requirements is mandatory for all BAC delivered capital projects. Please speak with Sustainability team if any concerns. Project teams must table all elements to determine relevant design elements to be incorporated into the Concept Design Report. If the project team deems an element to not be applicable to their project, they must provide a justification in the comments section, in the design report, as to the reason behind this decision. How to use: Property team is to use the Property Only tab. All other projects are to use use Deliverables, Design Report and Construction Report tabs. - Select if the sustainability element has been implemented in the final design. If it has not been included please advise in the comments section why it has not been included - Add continous comments throughout the different design stages in the comments section. - The Construction Organisation is to complete the Construction tab (Please note these are now part of BAC's Beakon monthly reporting- except embodied carbon) Referenced Documents: PSG-STD-005 Minimum Requirements – Design Services Landscaping Setting Strategy DDA Disability Discrimination Act DSAPT Disability Standards for Accessible Public Transport (2002) Disability (Access to Premises - Buildings) Standards 2010
Definitions
The terms used in this Airport Design Guideline shall be as defined in Table 1 below
Term | Definitions and Interpretations
ABC | Airport Building Controller
BAC | Brisbane Airport Corporation Pty Limited (Principal)
ADG | Airport Design Guideline required to satisfy; i.e. what the design is based on
AFS | Australian Forestry Standard
BAC | Brisbane Airport Corporation Pty Ltd
BMCS | Building Management Control Systems
C&D | Constuction and Demolition
CASA | Civil Aviation Safety Authority
CO2 | Carbon Dioxide
FSC | Forest Stewardship Council
GECA | Good Environment Choice Australia
GWP | Global Warming Potential
NCC | National Conustruction Code
PEFC | Programme for the Endorsement of Forest Certification
SRI | Solar Reflectance Index
SSA | Steel Sustainability Australia
TN | Total Nitrogen
TP | Total Phosphorous
TSS | Total Suspended Soil
VAV | Variable Air Volume
VOC | Volatile Organic Compound
WOL | Whole of Life
WSUD | Water Sensitive Urban Design
Document information
Current version | 4
Last updated
Review frequency | Annually
Review before | 2025-06-01
Document number
Owner | Engineering & Sustainability
Audience | BAC

## Deliverables
Guidelines for Project Deliverables
Task
Identify MSR's for the project with the Sustainability team (including obtaining and exceptions)
BAC Sustainability team to review the Sustainability Design Report and endorse project initiatives during the design development stages
Submit finalised Sustainability Design Report to the Engineering and Sustainability team at the completion of the design
Submit Sustainability Construction Report to the Engineering and Sustainability teams at the completion of the project.
Design Stage Deliverables
Mini, IT and Facilities projects do not have specific project deliveries during design development.
The specific design deliverables required for all other BAC projects are as defined in the following table.
Project Stage | Specific Documentation Required for this Design Element
Concept Design (30%) | Draft Sustainability Design Report
Schematic Design (50%) | Updated Sustainability Design Report
Developed Design (90%) | Updated Sustainability Design Report
Detailed Design (100%) | Finalised Sustainability Design Report
Construction Stage Deliverables
The construction deliverables listed in this section are additional specific requirements required by BAC
Construction Stage | Specific Documentation Required for this Design Element
Construction Deliverables | During construction the team is to submit their monthly Beakon sustainability report
Commissioning Deliverables | No additional requirements
Project Completion Deliverables | The Contractor shall submit the embodied carbon section of the construction tab
Governance Process

## Design Report
Sustainability Design Report (Template)
Criteria | Sustainability Element | Sustainability Element Incorporated (Yes/No/Maybe) | Design Target (If applicable) | Designers' Comment
Management | Establish project sustainability vision and goals (to be agreed with BAC Sustainability team and must include carbon and energy, water, waste and materials where applicable)
Measure, monitor and report the footprint of the project throughout design development and construction (carbon emissions, energy, waste generated, waste recycled, water and fuel usage)
All contractors to maintain an EMS in line with the principles of AS/NZS ISO 14001
All contractors to develop and implement a project-specific Construction Environmental Management Plan (CEMP) and Site Waste Management Plan (SWMP) on all projects to manage environmental performance, conditions and potential impacts arising from demolition, excavation or construction works
Comply with the requirements of ISO 20400 Sustainable Procurement
Whole Life Value | Conduct whole life cycle cost analysis and update throughout all phases of project development on selected initiatives in accordance with the guidance and principles of ISO 15686-5 and AS/NZS 4536 to determine capex and opex costs/savings
Carbon and Energy | All new buildings or new works within existing BAC buildings to incorporate passive design principles that respond to environmental conditions, including solar access, prevailing winds, seasonal/diurnal temperature changes to improve building envelope performance and reduce mechanical system cooling loads and energy consumption
10% increase in thermal performance for building envelope, lighting ect
The buildings energy use shall be at least 10% less than NCC Section J requirement
All building services are to minimise peak power loads on the electricity network and are considered the potential for thermal storage to generate chilled water at night, battery storage of power generated by onsite renewable energy sources and phase change materials in building finishes
Developments to use 100% renewable electricity either from either on-site solar generation or a green PPA by 2025
Maximum lamp or illumination power density factor of artificial lighting to meet NCC Section J DTS provisions for various indoor spaces not to exceed 14W/m2 (retail and food and beverage outlets inside terminals).
All lighting in designated pax areas is to be LED and flicker free with indoor lamps to be fitted with intelligent programmable sensor, occupant, and timer controls
All external lighting except emergency lighting to meet AS4282 requirements and to exceed minimum energy requirements and, where possible, specified with LED luminaires with photocell and manual override controls
Artificial lighting design shall be in accordance with the BAC Airport Design Guidelines and complement natural daylight provision, provide a high quality of general illuminance and be glare free in line with AS/NZS 1680.1
Increase perimeter daylight zones - extend the perimeter footprint to maximise the usable daylighting area
For new buildings, allow daylight penetration high in a space. Windows located high in a wall or in roof monitors and clerestories will result in deeper light penetration and reduce the likelihood of excessive brightness
For new buildings, slope ceilings to direct more light into a space
Avoid direct beam daylight on critical visual tasks
The building’s light pollution has been minimised in line with AS/NZS 4282
Recommend where façade elements are modified, replaced facade exceeds NCC Section J requirements by a minimum of 10%.
All public lounge and seating areas in terminals along with food courts to have a clear line of sight to high quality internal or external views
For all new buildings (based on an acceptable WOL assessment) air permeability rates to range between 2-5m3/m2/hr at 50pa for optimal airtightness, to minimise air leakage and ingress to the external environment. Air testing is required.
Install high efficiency (low energy) heating and cooling systems in accordance with BAC Airport Design Guidelines and shall be designed to be a minimum 10% better than NCC Section J requirements.
Install zoned variable air volume (VAV) boxes for cooling of perimeter zones with reduced cooling setpoints to 22oC-24oC (indoor setpoint temperature to be 23oC with +/- 1.5oC)
Hybrid timber and concrete structures will be considered to minimise the building’s embodied carbon footprint
Consider the feasibility of rooftops solar photovoltaic (PV) panels and supply renewable power on a project-by-project basis in line with BAC’s pathway to Net Zero by 2025.
Variable speed chilled water pumps and variable speed fans controlled at the minimum possible speed to satisfy demand loads
Low temperature variable-air volume air conditioning system that matches the air supply to the actual load (not the peak load)
Air Handling Unit Specific Fan Power (SFP) shall be 0.3-0.5W/l/s
Annual leakage from sealed refrigerant equipment and systems to be zero as far as practicable
All refrigerants to be a low Global Warming Potential (GWP) of less than 5 and 0 Ozone Depletion Potential (ODP)
Maintain indoor air temperature at 19oC-26oC and internal CO2 concentrations at less than 700ppm
Equip air conditioning systems with VOC and CO2 sensors to provide constant spatial air quality monitoring especially for indoor areas with high fluctuating footfall or dwelling population
All buildings to use enthalpy exchange between outside air entering a climate controlled zone and exhaust air existing the building from a climate controlled zone.
Smart meters (including sub-meter network) to be designed in accordance with BAC Airport Design Guidelines and be installed to monitor and record energy and water consumption across all building levels.
At least 15% of every development's solar-exposed areas when the sun is directly overhead, excluding facades, is to comprise green space with with trees, planted public realms and streetscapes.
Water | All projects to incorporate Water Sensitive Urban Design (WSUD) features to capture, filter, and reuse on-site water resources where practicable, and to reduce the concentrations of suspended solids (TSS), phosphorous (TP) and nitrogen (TN) via nutrient uptake, denitrification through vegetated soil media filters and permeable conveyance
Targeting storm water, site discharges are not to increase the natural average load of nutrients and sediments in line with Brisbane Airport Stormwater Quality Management Guideline
All water fittings and fixtures to be low flow and efficient with the best avaliable WELS rated for fixtures
Consider the feasibility of rainwater harvesting to complement BAC’s recycled water network and property utilisation and where practicable install rainwater capture tank to retain water for non-potable uses including WC/urinal flushing sized at 10L/m2
All public realm and streetscapes to be in line with the Brisbane Airport Landscape Setting Strategy March 2018
All landscape irrigation systems comprising sprinklers or subsoil drip systems fitted with water timers and rain and moisture sensors to meet Queensland Government Guidelines for Irrigation and Water Conservation
Use mulch in all landscaped areas to minimise evaporative water loss through the soil
Waste | Divert at least 90% of the project's C&D waste (by weight) from landfill (i.e. percentage benchmark); or Send less than 10 kg of C&D waste to landfill per m2 of GFA (i.e. fixed benchmark) * Special waste streams (e.g., asbestos waste or other hazardous materials) are excluded from consideration
Adopt circular economy principles for building materials and products prioritising those that can be disassembled, recycled, or up cycled and/or have been previously used to help close the loop on material flows and improve resource efficiency
Where feasible, consider specifying the use of prefrabricated construction methods to reduce offcuts and other sources of construction waste
Best available waste separation and collection systems to be installed to maximise at-source segregation for reuse and recycling
Design in to allow the 100% composting and recycling of all organic and food waste
Materials | At least 20% of materials, by cost, comply with one of the following criteria: - Reused product - Contain recycled content - Have an Environmental Product Declaration - Posses third-party certification (e.g. GECA, GreenTag GreenRate, etc.)
The upfront carbon emissions from materials and products have been reduced as much as possible
If possible, more than 70% of construction materials (by cost) to be locally sourced within 750km
Preference shall be given to materials that contain recycled content (structural/reinforcing steel, concrete, aggregates, pavement base course layers, bricks, ashphalt, furniture, water)
If possible, all hardwood and softwood timber or timber-derived products to be from 100% Australian Forestry Standard (AFS), Forest Stewardship Council (FSC) or Programme for the Endorsement of Forest Certification (PEFC) accredited forest certified sources accompanied by relevant chain of custody documentation
For new builds, where practical, at least 30% of the Gross Floor Area (m2) to be constructed or supported by structural compliant timber from AFS or FSC or PEFC-certified sources
At least 60% (by mass) of all fabricated structural steelwork like reinforcing bar and mesh (for steel-framed buildings) to be sourced from a steel contractor accredited to the Environmental Sustainability Charter of the Australian Steel Institute
All projects to use concrete mix with reduced Portland Cement content by a target of at least 40% where applicable, replaced with supplementary cementitious materials, e.g., fly ash. Where suitable BAC's preference is to use low carbon concrete
Only use non toxic or low VOC emitting materials for internal use applied to paints, solvents, sealants, adhesives, wood products.
All PVC products (100%) to meet Best Practice Guidelines for PVC in the Built Environment
Consider using furniture products that have been certified by Good Environmental Choice Australia (GECA)
Incorporate cool pavements, SRI approved roof materials and paint systems to reduce the airport’s UHI effect and that are in accordance with CASA’s anti-glare requirements for aeronautical safety
Health | Levels of indoor pollutants are mainted to acceptable levels
A high level of outdoor air is provided with pollutant entering the building being minimised
The building is designed and constructed to be accessible and inclusive to a diverse range of people with different needs.
The building achieves the acoustic requirements as specified in BAC's Airport Design Guidelines
Site layout to provide connectivity to existing and proposed network of pedestrian and cycle paths throughout all primary and secondary routes within the development
Provide cycle parking and end of trip facilities. Cycle parking to be shaded, in preferential locations and include space for future expansion
Universal Design | Automatic door for all PWD toilet and change rooms public access
Consider placement of quite room
Where this can be achieved, consider creating opportunities for shorelining’ for guests who are blind or low vision to negotiate
Provide designated accessibility tables and chairs that are height adjustable and can be moved at work points/eating areas.
Elevator functionality to include a destination audio description
Consideration of materials that will absorb sound and reduce reverberation (i.e., flooring and sound absorbing materials on walls).
Prioritise the use of natural light where possible to reduce eye fatigue and assist with circadian rhythm
Where it can be achieved, provide areas with low lighting or where lighting can be adjusted (ie parent room)
Ensure consistency of lighting –amenity lighting should range from warm white light (2 700 K) to cool white light (4 000 K)
Limit patterns which may cause sensory / visual overload and discomfort – ie stripes and geometric patterns with high contrast and uncomfortable patterns in three dimensional forms should be avoided.
Matt or low-sheen to be considered to reduce glare – ensure floor and wall surfaces have low reflectance
Consider using muted colours, as they are typically more calming (i.e., greens and light, warm neutral tones) and cause less sensory overload than vivid colour
Technology | Internet of Things (IoT) and smart building technologies - IoT devices and sensors embedded within buildings can collect data on energy consumption, indoor air quality, occupancy patterns, and more. Through use smart building technologies, dynamic control of lighting, heating, and ventilation systems based on real-time data, leading to energy savings can be enabled
Resilience | Develop a project specific climate change risk and adaptation assessment for the building (speak with Sustainability team)
At least 75% of the whole site area comprises of one or a combination of strategies that reduce the heat island effect

## Design Report (Property)
Property 1. Incorporate all Mandatory Sustainable Initiatives in the design and delivery of the development (listed in the table below); and 2. Identify and incorporate Other Sustainable Initiatives, at the tenderer’s discretion. For an allignment to a 4 star Green Star a minimum of 15 points is required. For a 5 star Green Star certification a minimum of 35 points is required 3. This document is to go out with tenders in annex as a word document. 4. The successful tenderer will be required to track and report on the inclusion of the Mandatory Sustainable Initiatives and the selected Other Sustainable Initiatives. 5. Contractor is to provide an indepenedent report and include all items from email - 31.3 use ESD
Sustainability Design Report for Property Delivered Projects (Template)
| Mandatory Sustainability Initiatives | Green Star Building (Submission Guideline) Credit No. | Requirement | Points | Initial Review | Designers' Comments
1 | Responsible Construction | Credit 2 | The site must have an environmental management plan covering the scope of construction activities. | M | M
The builder must have an environmental management system (large builders will need to be ISO14001 accredited).
80% of construction and demolition waste must be recycled.
2 | Verification and Handover | Credit 3 | The building must be commissioned and tuned and set up for ongoing management with appropriate metering and monitoring systems | M | M
The builder must create and deliver operations and maintenance information to the facilities team at the time of handover.
3 | Responsible Management Resource | Credit 4 | The building is designed for the collection of 3 separate waste streams and must have appropriate spaces for waste management with an appropriately sized loading dock. | M | M
4 | Clean Air | Credit 10 | The ventilation system must have appropriate filtration. | M | M
Point source pollutants must be exhausted directly outside (printers, kitchens).
The building must be provided with at an adequate amount of outside air.
5 | Light Quality | Credit 11 | Lighting within the building meets minimum comfort requirements | M | M
Good lighting levels suitable for the typical tasks in each space
The building provides adequate levels of daylight
6 | Acoustic Comfort | Credit 12 | An Acoustic Comfort Strategy must be prepared describing how the building design will deliver acoustic comfort to the building occupants. | M | M
7 | Exposure to Toxins | Credit 13 | All the paints, adhesives, sealants, and carpets must have low levels of Volatile Organic Compounds. Engineered wood must be low formaldehyde. There must be no lead, asbestos, and PCBs in the building. | M | M
8 | Upfront Carbon Emissions | Credit 21 | The building has 10% less upfront carbon emissions compared to a standard building from materials. | M | M
9 | Energy Use | Credit 22 | The building has at least a 10% lower energy consumption than one built to the National Construction Code 2019. | M | M
10 | Water Use | Credit 25 | The building has at least a 15% reduction in potable water usage when compared to a reference building | M | M
OR
The building installs water efficient fixtures and appliances.
11 | Movement and Place | Credit 27 | The building includes showers and changing facilities for building occupants | M | M
The facilities are accessible, inclusive and located in a safe and protected space.
12 | Inclusive Construction Practices | Credit 31 | During construction, the builder provides gender inclusive facilities and protective equipment and implements policies on site to increase awareness and reduce instances of discrimination, racisms and bullying. | M | M
| Impacts to Nature | Credit 35 | The building was not built on, or significantly impacted, a site with a high ecological value. | M | M
The building’s light pollution has been minimised.
There is ongoing monitoring, reporting, and management of the site’s wetland ecosystem.
| Other Sustainable Initiatives | Green Star Building (Submission Guideline) Credit No. | Requirement | Points | Initial Review | Designers' Comments
1 | Responsible Construction | Credit 2 | 90% of construction and demolition waste is diverted from landfill. | 1
2 | Verification and Handover | Credit 3 | An independent level of verification is provided to the design, planning, commissioning and tuning activities through the involvement of an independent commissioning agent. | 1
3 | Responsible Procurement | Credit 5 | The building’s design and construction procurement processes follow ISO20400 Sustainable Procurement – Guidance by undertaking a risk and opportunities assessment. | 1
A responsible procurement plan is developed to mitigate risks and implement opportunities identified in the assessment.
4 | Responsible Structures | Credit 6 | 50% of all structural components (steel, timber, concrete etc.) meet a responsible products value of at least 10% | 3
5 | Responsible Finishes | Credit 9 | 40% of all internal building finishes (by area) meet a Responsible Products Value score of at least 7 | 1
6 | Clean Air | Credit 10 | The building’s ventilation systems allow for easy maintenance. | 2
A high level of outdoor air is provided.
Any mechanical ventilation system must provide adequate access to both sides of all moisture and debris-catching components for maintenance within the air distribution system.
7 | Light Quality | Credit 11 | The building provides best practice artificial lighting | 2
OR
The building provides best practice access to daylight
8 | Light Quality - Exceptional | Credit 11 | The building provides best practice artificial lighting | 2
AND
The building provides best practice access to daylight.
9 | Acoustic Comfort | Credit 12 | A combination of the following are achieved: | 2
The building achieves maximum internal noise levels
AND / OR
The building achieves minimum internal noise levels
AND / OR
The building provides acoustic separation
AND / OR
The building minimises impact noise transfer
AND / OR
The building is designed with reverberation control
10 | Exposure to Toxins | Credit 13 | On-site tests verify the building’s paints, sealants are carpets have low Volatile Organic Compounds (VOC) and formaldehyde levels. | 2
11 | Amenity and Comfort | Credit 14 | The building has dedicated amenity rooms to act as a parent room, relaxation room, or an exercise room. | 2
12 | Climate Change Resilience | Credit 16 | The project team develops a project-specific climate change risk and adaptation assessment for the building. | 1
Extreme and high risks are addressed.
13 | Heat Resilience | Credit 19 | At least 75% of the whole site comprises of one or a combination of strategies that reduce the heat island effect. | 1
14 | Grid Resilience | Credit 20 | The building provides active generator and storage systems | 3
AND / OR
The building has the infrastructure to deliver an appropriate demand response strategy
AND / OR
The building has reduced its electricity consumption through passive design
15 | Upfront Carbon Emissions | Credit 21 | The building's upfront carbon emissions are at least 20% less than those of a reference building and must occur through good design and material selection. | 3
Demolition works are offset
16 | Energy Use | Credit 22 | Building energy use is 20% less than a reference building. | 3
17 | Energy Use – Exceptional | Credit 22 | Building energy use is 30% less than a reference building. | 3
18 | Energy Source | Credit 23 | 100% of the building's electricity sourced from renewable electricity. | 3
19 | Energy Source- Exceptional | Credit 23 | 100% of the building's energy (all non-electricity related energy) sourced from renewable energy | 3
| Other Carbon Emissions | Credit 24 | The building owner eliminates emissions from refrigerants or the building owner offsets emissions from refrigerants | 2
20 | Water Use | Credit 25 | The building uses 45% less potable water compared to a reference building. | 3
The building has infrastructure for recycled water connection
21 | Life Cycle Impacts | Credit 26 | The project demonstrates a 30% reduction in life cycle impacts when compared to standard practice. | 2
22 | Inclusive Construction Practices | Credit 31 | Policies and programs implemented are relevant to construction workers on site | 1
Builder provides high quality staff support on-site to reduce at least five key physical and mental health impacts
The effectiveness of interventions is evaluated
23 | Design for Inclusion | Credit 34 | The building is design and constructed to be inclusive to a diverse range of people with different needs. | 2
|  |  |  | 49 | 0
Alignment with 4 Star Green Star a minimum of 15 points is required
Alignment with 5 Star Green Star a minimum of 35 points is required

## Construction Report
Environmental Sustainability Construction Report
Project Details
Project Name:
Asset Type:
BAC Project No:
BAC Project Manager
End of project Upfront Carbon Achievements
Sustainability Target | Design Target | Actual Achieved Performance
Upfront Carbon | concrete - kg and % asphalt - kg and % steel - kg and % timber - kg and % builders rubble - kg and % electronic waste - kg and % | concrete - kg and % asphalt - kg and % steel - kg and % timber - kg and % builders rubble - kg and % electronic waste - kg and %
Beakon Monthly Reporting Requirements
Renewable Energy | mW and % | mW and %
Water Consumption | potable water - kL recycled water - kL | potable water - kL recycled water - kL
Waste Generation (ie sent offsite to landfill) | concrete - kg and % asphalt - kg and % steel - kg and % timber - kg and % builders rubble - kg and % electronic waste - kg and % | concrete - kg and % asphalt - kg and % steel - kg and % timber - kg and % builders rubble - kg and % electronic waste - kg and %
Material Reuse (ie reused material on airport) | concrete - kg and % asphalt - kg and % steel - kg and % timber - kg and % pavement gravels - kg and % fill material - kg and % | concrete - kg and % asphalt - kg and % steel - kg and % timber - kg and % pavement gravels - kg and % fill material - kg and %
Waste Recycling (ie material sent to recycling facility) | concrete - kg and % asphalt - kg and % steel - kg and % timber - kg and % builders rubble - kg and % electronic waste - kg and % | concrete - kg and % asphalt - kg and % steel - kg and % timber - kg and % builders rubble - kg and % electronic waste - kg and %
Other Contractor Activities | not applicable | fuel usage - L renewable fuels - L and/or kW
Other Targets that are not stated above | as applicable | as applicable

## Sheet1 (hidden)
Drop down box 1 | Drop down box 2
Y | Y
N | N
N/A | Maybe